|  | ......................... Stk. .............................. € .............................. € GEZE MCRdrive Automatic, hermetically sealing MCRdrive linear sliding door system for inner areas with air permeability requirements according to EN1026 / EN 12207 class B / 100 Pa, class C / 50 Pa. Noise insulation in accordance with DIN EN ISO 4109. TÜV type-tested in accordance with DIN 18650 / EN 16005, for leaf weights up to 140 kg with MCR fine-framed profile system. The system consists of the primary assemblies: Drive unit with specialised software for OR sliding doors Door leaf system with fine-framed profiles and full circumferential sealing system Construction dimensions (dimensions in unfinished state): Passage clearance DB:............. mm (800 - 2500 mm) Passage height DH:.............. mm (2000 – 2500 mm) Door system version: ( ) single leaf right hand slide to open ( ) single leaf left hand slide to open |
| --- | --- |
|  | ......................... Stk. .............................. € .............................. € MCR drive unit and GEZE control unit Dimensions of drive unit H x D: 300 x 185 mm Automatic door drive consisting of: Integrated rechargeable battery with automatic charging and monitoring Extremely quiet DC drive Aluminium track and roller carriage with plastic track rollers, including articulated joint for lowering and pressing the door leaf to the wall connection profile for the hermetic seal Rugged power supply with integrated multipolar main switch and fuse. Static and dynamic power limitation according to DIN 18650 / EN 16005, as well as static under 150 N in compliance with ASR A1.7 (formerly BGR 232) Intelligent control (category 2 in accordance with DIN EN 954-1 and Performance Level “D” in accordance with DIN EN ISO 13849-1) Convenient parameter setting, commissioning and maintenance via optional Bluetooth connection to a PC Self-learning and with dynamic adaptation of the passage hold-open time for optimum convenience Can be connected to and integrated in building management systems via CAN bus Independent error recognition and recording Adjustment options for all door movement parameters All functions integrated in one unit, no further modules necessary Automatic reversing in case of obstacle detection Drive functions: various Push & Go functions available Various types of opening and opening widths optimised for use in medical areas (nurse opening, bed opening, cleaning opening) available for selection Freely configurable inputs and outputs for different functions Integrated rechargeable battery for emergency opening and closing in the event of a power failure Wiring to be carried out on site according to the GEZE cable plan by an electrical contractor. Installation, commissioning and instruction of the operator as well as documentation handover in compliance with DIN 18650 / EN 16005 through plant fitters or service partner. In accordance with DIN 18650 / EN 16005: Safety analysis must be carried out as a basis for planning and execution An inspection must be carried out at least 1 x year and maintenance at least 1 x year |
|  | ......................... Stk. .............................. € .............................. € MCR profile and sealing system Air tightness and seal are ensured on all four sides of the leaf via a lowering and simultaneous pressing movement of the leaf against the on-site frame. The full circumferential sealing system consists of a specialised balloon seal and a concealed 2-chamber seal in the foot area. Vulcanised sealing corners are used to guide the full circumferential seal. The seals are installed in sealing grooves integrated into the profile. ( ) fine-framed aluminium profile system, up to 140 kg leaf weight, for panel thickness up to 22 mm ( ) single glazing ( ) 2 panes of ISO glass ( ) toughened safety glass ( ) laminated safety glass ( ) HPL ( ) stainless steel panel The glazing can be designed both as dry glazing with system-side seals for different panel thicknesses, or as wet glazing. |
|  | ......................... Stk. .............................. € .............................. € Operation GEZE display programme switch in the AS500 programme for setting the mode of operation as well as for commissioning and parameter setting of the drive, with control keys, 2 x 7 segment display, alphanumeric error display, IP rating IP40 Modes of operation: permanently open, automatic, exit only, night-locking, off ( ) Surface-mounted ( ) Flush-mounted Or GEZE keypad programme switch for setting the mode of operation, with function keys, LED dot display, coded error display, IP40 rating, suitable for switch product ranges with 55 x 55 mm switch unit Modes of operation: off, permanently open, automatic, exit only, night-locking ( ) Surface-mounted ( ) Flush-mounted Or GEZEconnects Bluetooth RS485 interface for the wireless connection between computer and automatic door drives. Or GEZE mechanical programme switch for setting the mode of operation, with rotary knob, LED error display, IP40 rating, suitable for switch product ranges with 55 x 55mm switch insert Modes of operation: off, permanently open, automatic, exit only, night-locking ( ) Surface-mounted ( ) Flush-mounted Or GEZE mechanical programme switch for setting the mode of operation, with key, LED error display, IP40 rating, suitable for switch product ranges with 55 x 55mm switch insert Modes of operation: off, permanently open, automatic, exit only, night-locking ( ) Surface-mounted ( ) Flush-mounted |
|  | ......................... Stk. .............................. € .............................. € Operation (optional position) GEZE key switch to “lock” the programme switch to prevent unauthorised changing of the mode of operation, IP40 rating ( ) Surface-mounted ( ) Flush-mounted |
|  | ......................... Stk. .............................. € .............................. € Activation and protection GEZE combined detector with direction-sensing radar movement detector and self-monitored double 3D light curtain for activation and protection of the closing section in accordance with DIN 18650 / EN 16005, IP54 rating ( ) combined detector interior ( ) combined detector exterior |
|  | ......................... Stk. .............................. € .............................. € Protection (optional position) GEZE active infrared detector with double 3D light curtain for protecting the opening or closing area according to DIN 18650 / EN 16005, IP54 rating ( ) interior ( ) exterior |