|  | ......................... pcs. .............................. € .............................. € GEZE locking drive Power lock For the safe locking and unlocking of vertically installed and inward opening bottom-hung, top-hung and side-hung casements as well as outward opening top-hung casements Modular system with set on electric drive with integrated sequence control in combination with the GEZE electric chain drives Slimchain, Powerchain and the electric spindle drive E 250 NT Locking and unlocking of window casements through driver pins on the central closure. Special features: - Automatic adjustment of final position - Actuation of euronut and system push-rods - Variable installation for casement or frame installation - Driver can be turned through 180° - Drive can be mounted on the left and right Drive can be unlocked even in the closed state. Technical data: Locking stroke: 22 mm Tensile force/pressure: max. 600 N Opening/closing time: max. 6 s Voltage: 24 V Current consumption: 1.5 A Enclosure rating: IP 42 Ambient temperature: -5 °C to +70 °C Connection cable: 2 m*, silicon sheathed Opening mechanism: Stainless steel driver * Special length on request GEZE locking drive Power lock is suitable for installation in tested and certified GEZE SHEVs in accordance with EN 12101-2. Version: Solo ( ) Syncro ( ) Type of installation: ( ) set on Type of window: ( ) Bottom-hung casement ( ) Top-hung casement ( ) Side-hung casement ( ) inward opening ( ) outward opening Casement material: ( ) Aluminium ( ) Plastic ( ) Wood Colour: ( ) EV1 ( ) white RAL 9016 ( ) according to RAL ........ Note: When used on bottom-hung casements, we prescribe the use of separate safety scissors (2 pieces) for product liability reasons, e.g. GEZE safety scissors no. 35 or no. 60. |
| --- | --- |
|  | ......................... pcs. .............................. € .............................. € ( ) Accessory set casement installation |
|  | ......................... pcs. .............................. € .............................. € ( ) Accessory set frame installation EV1 |
|  | ......................... pcs. .............................. € .............................. € ( ) Accessory set frame installation RAL 9016 |
|  | ......................... pcs. .............................. € .............................. € ( ) Accessory set frame installation according to requirement |
|  | ......................... pcs. .............................. € .............................. € Installation and functional test Installation and functional test by an expert authorised by the manufacturer. |
|  | ......................... pcs. .............................. € .............................. € Start-up and official approval Official approval of the complete smoke and heat extraction system by an officially recognised expert, who also hands over the acceptance certificates. |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - compact package Maintenance and testing of hold-open systems (optional position) Service package for maintenance and testing according to ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - comfort package Service maintenance (optional position) Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
|  | ......................... pcs. .............................. € .............................. € Delivery and installation Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan. Delivery, installation and commissioning through plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in an inspection log. |