|  | ......................... pcs. .............................. € .............................. € GEZE electric chain drive Powerchain for a smoke and heat extraction system For daily aeration and ventilation and safe and fast smoke and heat exhaust and smoke extraction on vertically or angled installed, inward and outward opening bottom-hung, top-hung, and side-hung casements as well as for light domes and skylights. Electric chain drive as a direct opener in 24 V version. The drive must be activated via a micro-processor. A distinction can be made between alarm and ventilation operating speed. The opening width and operating speed in ventilation mode can be programmed individually via software. The drive is equipped with electronic end position cut-off and overload protection and has electronically regulated soft start and soft stop. The control is carried out via a GEZE emergency power control unit in the event that the smoke and heat extraction system is triggered. Daily use of the ventilation function is carried out using the GEZE vent switch. Synchronised multiple operation of up to 3 drives must be guaranteed without additional external module. Activation and adjustment of the synchro function is by means of integrated DIP switches without additional programming being necessary. Automatic switch-off when the end position is reached. Overload protection when opening and closing. Sealing via electronically defined pressure. Drive fixtures and chain attachments allow quick and easy installation from the front. Technical data: Stroke: 600/800 and 1200 mm Tensile force/pressure: 600 N/max. 600 N, stroke-dependent Voltage: 24 V DC / 230 V with external mains adapter Current consumption: RWA (18 V) 1.5 A, ventilation (24 V) 1.2 A Enclosure rating: IP 40 Ambient temperature: -5 °C to +70 °C Connection cable: 2 m*, silicon sheathed * Special length on request The GEZE chain drive Powerchain is suitable for installation in tested and certified GEZE SHEVs in accordance with EN 12101-2. Version: Solo ( ) Syncro ( ) Type of installation: ( ) supported Type of window: ( ) Bottom-hung casement ( ) Top-hung casement ( ) Side-hung casement ( ) Skylights ( ) inward opening ( ) outward opening Other types of casement available on request Casement dimensions: ........ mm width (min. 760 mm) ........ mm height (min. 400 mm, depending on the type of window, panel weight or casement weight, stroke and type of installation) Casement material: ( ) Wood ( ) Aluminium ( ) Plastic Opening width: ........ mm or max. ....... mm (to be completed by the bidder) Colour: ( ) EV1 ( ) white RAL 9016 ( ) according to RAL ........ Note: When used on bottom-hung casements, we prescribe the use of separate safety scissors (2 pieces) for product liability reasons, e.g. GEZE safety scissors no. 35 or no. 60. Note: In order to guarantee the performance classes as set out in DIN EN 14351-1 with regard to wind load, sealing in the event of rain and air tightness, an additional locking mechanism must be planned on the window according to the specifications of the profile system manufacturer, e.g. GEZE Power lock. |
| --- | --- |
|  | ......................... pcs. .............................. € .............................. € ( ) Bracket set Powerchain type A (bottom-hung) ( ) Bracket set Powerchain type B (top-hung) |
|  | ......................... pcs. .............................. € .............................. € ( ) Safety scissors (2 pcs.) |
|  | ......................... pcs. .............................. € .............................. € Note: You also require an emergency power control unit GEZE E 260 N, THZ, THZ Comfort or MBZ 300 and accessories. |
|  | ......................... pcs. .............................. € .............................. € Installation and functional test Installation and functional test by an expert authorised by the manufacturer. |
|  | ......................... pcs. .............................. € .............................. € Start-up and official approval Official approval of the complete smoke and heat extraction system by an officially recognised expert, who also hands over the acceptance certificates. |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - compact package Maintenance and testing of hold-open systems (optional position) Service package for maintenance and testing according to ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - comfort package Service maintenance (optional position) Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
|  | ......................... pcs. .............................. € .............................. € Delivery and installation Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan. Delivery, installation and commissioning through plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in an inspection log. |